## Area Requirements
PROJECT INFORMATION
Gross Floor Area (m2) | 2000
Area Per Floor (m2) | 500
Floor to Floor Height (m) | 4
Occupancy Density (people/m2) | 0.04 |  | From ASHRAE 62.1-2019, Table 6.1
Total Occupancy (people) | 80
Occupancy Per Floor (people/floor) | 20
TYPICAL FLOOR AREA REQUIREMENTS
MEP Area (m2) | 1.7474
Elevator Area (m2) | 5.75 | ONE ELEVATOR SHAFT
Egress Stair Area (m2) | 6.768 | ONE EGRESS STAIR
ROOF AREA REQUIREMENTS
MEP Area (m2) | 78.9623 | FAN ROOM + ELEVATOR MACHINE ROOM
MECHANICAL SYSTEMS
Cooling Load (kW) | 151.2645
Cooling Load (tons) | 29.985 |  | From Mechanical and Electrical Equipment for Buildings, 10.3, Table 10.5
Airflow Rate (m3/hr) | 20401.7991 |  | From Mechanical and Electrical Equipment for Buildings, 10.3, Table 10.5
Airflow Rate (m3/s) | 5.6672
Supply Shaft Area (m2) | 0.82372 | TYPICAL FLOOR (CORE) | From Mechanical and Electrical Equipment for Buildings, 10.4 (a) Air Ducts
Return Shaft Area (m2) | 0.82372 | TYPICAL FLOOR (CORE)
Heating and Cooling Area Pipe Riser Area (m2) | 0.1 | TYPICAL FLOOR (CORE) | From The Architect's Studio Companion, 4, Vertical Distribution of Services for Large Buildings
Central Fan Room Area (m2) | 53.9623 | BASEMENT, ROOF, MEP ROOM | From Mechanical and Electrical Equipment for Buildings, 10.2, Table 10.3
Central Boiler and Chiller Room Area (m2) | 20.0498 | BASEMENT OR ROOF | From Mechanical and Electrical Equipment for Buildings, 10.2, Table 10.3
ELECTRICAL SYSTEMS
Electrical Room (m2) | 2 | BASEMENT OR ROOF | From The Architect's Studio Companion, 4, Major Equipment Spaces for Large Buildings
PLUMBING SYSTEMS
Water Pump Room (m2) | 8 | BASEMENT OR ROOF | From The Architect's Studio Companion, 4, Major Equipment Spaces for Large Buildings
Fire Pump Room (m2) | 8 | BASEMENT OR ROOF | From The Architect's Studio Companion, 4, Major Equipment Spaces for Large Buildings
VERTICAL TRANSPORTATION
Number of Elevator Shafts | 1 |  | From The Architect's Studio Companion, 4, Major Equipment Spaces for Large Buildings
Individual Shaft Area (m2) | 5.75 | TYPICAL FLOOR (CORE) | From The Architect's Studio Companion, 4, Major Equipment Spaces for Large Buildings
Elevator Machine Room Area (m2) | 25 | ROOF | From The Architect's Studio Companion, 4, Major Equipment Spaces for Large Buildings
EGRESS STAIRS
Width Per Occupant (mm) | 8 |  | From The Architect's Studio Companion, 5.2, Sizing the Egress System
Occupant Load | 53.7634 |  | From The Architect's Studio Companion, 5.2, Sizing the Egress System
Number of Egress Stairs | 1 |  | From The Architect's Studio Companion, 5.2, Sizing the Egress System
Clear Width of Corridor and Stair (m) | 0.9 |  | From The Architect's Studio Companion, 5.2, Sizing the Egress System
Length of Egress Stair Enclosure (m) | 3.76 | TYPICAL FLOOR (CORE) | From The Architect's Studio Companion, 5.2, Sizing the Egress System
Width of Egress Stair Enclosure (m) | 1.8 | TYPICAL FLOOR (CORE)