## AREA REQUIREMENTS
PROJECT INFORMATION
Gross Floor Area (m2) | 5000
Area Per Floor (m2) | 1250
Floor to Floor Height (m) | 4
Occupancy Density (people/m2) | 0.04 |  | From ASHRAE 62.1-2019, Table 6.1
Total Occupancy (people) | 200
Occupancy Per Floor (people/floor) | 50
TYPICAL FLOOR AREA REQUIREMENTS
Mechanical Shaft Area per Floor (m2) | 5.4947 | SUPPLY AND RETURN RISERS
Electrical and Plumbing Room Area per Floor (m2) | 0 | ELECTRICAL AND PLUMBING RISERS
Elevator Area per Floor (m2) | 5.75 | TWO ELEVATOR SHAFTS
Egress Stair Area per Floor (m2) | 6.768 | TWO EGRESS STAIRS
ROOF AREA REQUIREMENTS
MEP Area (m2) | 164.5382 | FAN ROOM, COOLING TOWERS, ELEVATOR MACHINE ROOM
MECHANICAL SYSTEMS
Cooling Load (tons) | 90.9091 |  | From Mechanical and Electrical Equipment for Buildings, 10.3, Table 10.5
Airflow Rate (m3/hr) | 61854.5455 |  | From Mechanical and Electrical Equipment for Buildings, 10.3, Table 10.5
Airflow Rate (m3/s) | 17.1818
Supply Shaft Area (m2) | 2.4974 | TYPICAL FLOOR (CORE) | From Mechanical and Electrical Equipment for Buildings, 10.4 (a) Air Ducts
Return Shaft Area (m2) | 2.4974 | TYPICAL FLOOR (CORE)
Heating and Cooling Area Pipe Riser Area (m2) | 0.5 | TYPICAL FLOOR (CORE) | From The Architect's Studio Companion, 4, Vertical Distribution of Services for Large Buildings
Central Fan Room Area (m2) | 127.0382 | BASEMENT, ROOF, MEP ROOM | From Mechanical and Electrical Equipment for Buildings, 10.2, Table 10.3
Central Boiler and Chiller Room Area (m2) | 52.6188 | BASEMENT OR ROOF | From Mechanical and Electrical Equipment for Buildings, 10.2, Table 10.3
Cooling Tower Area (m2) | 12.5 | GROUND LEVEL OR ROOF | From Mechanical and Electrical Equipment for Buildings, 10.3 (c) Condensing Water Equipment
ELECTRICAL SYSTEMS
Electrical Room (m2) | 2 | BASEMENT OR ROOF | From The Architect's Studio Companion, 4, Major Equipment Spaces for Large Buildings
PLUMBING SYSTEMS
Water Pump Room (m2) | 8 | BASEMENT OR ROOF | From The Architect's Studio Companion, 4, Major Equipment Spaces for Large Buildings
Fire Pump Room (m2) | 8 | BASEMENT OR ROOF | From The Architect's Studio Companion, 4, Major Equipment Spaces for Large Buildings
VERTICAL TRANSPORTATION
Number of Elevator Shafts | 1 |  | From The Architect's Studio Companion, 4, Major Equipment Spaces for Large Buildings
Individual Shaft Area (m2) | 5.75 | TYPICAL FLOOR (CORE) | From The Architect's Studio Companion, 4, Major Equipment Spaces for Large Buildings
Elevator Machine Room Area (m2) | 25 | ROOF | From The Architect's Studio Companion, 4, Major Equipment Spaces for Large Buildings
EGRESS STAIRS
Width Per Occupant (mm) | 8 |  | From The Architect's Studio Companion, 5.2, Sizing the Egress System
Occupant Load | 134.4086 |  | From The Architect's Studio Companion, 5.2, Sizing the Egress System
Number of Egress Stairs | 1 |  | From The Architect's Studio Companion, 5.2, Sizing the Egress System
Clear Width of Corridor and Stair (m) | 0.9 |  | From The Architect's Studio Companion, 5.2, Sizing the Egress System
Length of Egress Stair Enclosure (m) | 3.76 | TYPICAL FLOOR (CORE) | From The Architect's Studio Companion, 5.2, Sizing the Egress System
Width of Egress Stair Enclosure (m) | 1.8 | TYPICAL FLOOR (CORE)