## AREA REQUIREMENTS
PROJECT INFORMATION
Gross Floor Area (m2) | 5000
Area Per Floor (m2) | 1250
Floor to Floor Height (m) | 4
Occupancy Density (people/m2) | 0.05 |  |  | From ASHRAE 62.1-2019, Table 6.1
Total Occupancy (people) | 250
Occupancy Per Floor (people/floor) | 62.5
TYPICAL FLOOR AREA REQUIREMENTS
Mechanical Shaft Area per Floor (m2) | 7.9246 | x1 | SUPPLY AND RETURN RISERS
Electrical and Plumbing Room Area per Floor (m2) | 13.2 | x1 | ELECTRICAL AND PLUMBING RISERS
Elevator Area per Floor (m2) | 5.75 | x2 | TWO ELEVATOR SHAFTS
Egress Stair Area per Floor (m2) | 6.768 | x2 | TWO EGRESS STAIRS
ROOF AREA REQUIREMENTS
MEP Area (m2) | 183.6005 | x1 | FAN ROOM, COOLING TOWERS, ELEVATOR MACHINE ROOM
MECHANICAL SYSTEMS
Cooling Load (tons) | 135.1351 |  |  | From Mechanical and Electrical Equipment for Buildings, 10.3, Table 10.5
Airflow Rate (m3/hr) | 91945.9459 |  |  | From Mechanical and Electrical Equipment for Buildings, 10.3, Table 10.5
Airflow Rate (m3/s) | 25.5405
Supply Shaft Area (m2) | 3.7123 |  | TYPICAL FLOOR (CORE) | From Mechanical and Electrical Equipment for Buildings, 10.4 (a) Air Ducts
Return Shaft Area (m2) | 3.7123 |  | TYPICAL FLOOR (CORE)
Heating and Cooling Area Pipe Riser Area (m2) | 0.5 |  | TYPICAL FLOOR (CORE) | From The Architect's Studio Companion, 4, Vertical Distribution of Services for Large Buildings
Central Fan Room Area (m2) | 146.1005 |  | BASEMENT, ROOF, MEP ROOM | From Mechanical and Electrical Equipment for Buildings, 10.2, Table 10.3
Central Boiler and Chiller Room Area (m2) | 90.6533 |  | BASEMENT OR ROOF | From Mechanical and Electrical Equipment for Buildings, 10.2, Table 10.3
Cooling Tower Area (m2) | 12.5 |  | GROUND LEVEL OR ROOF | From Mechanical and Electrical Equipment for Buildings, 10.3 (c) Condensing Water Equipment
ELECTRICAL SYSTEMS
Electrical Switchgear and Transformer Room (m2) | 82.8 |  | BASEMENT OR ROOF | From The Architect's Studio Companion, 4, Major Equipment Spaces for Large Buildings
Generator Room (m2) | 20.35 |  | GROUND LEVEL OR ROOF | From The Architect's Studio Companion, 4, Major Equipment Spaces for Large Buildings
Number of Electrical Closets Per Floor | 0.625 |  |  | From The Architect's Studio Companion, 4, Vertical Distribution of Services for Large Buildings
Electrical Closet Area (m2) | 8 |  | TYPICAL FLOOR (CORE) | From The Architect's Studio Companion, 4, Vertical Distribution of Services for Large Buildings
Telecommunications Closet Area (m2) | 1.8 |  | TYPICAL FLOOR (CORE) | From The Architect's Studio Companion, 4, Vertical Distribution of Services for Large Buildings
PLUMBING SYSTEMS
Water Pump Room (m2) | 9.25 |  | BASEMENT OR ROOF | From The Architect's Studio Companion, 4, Major Equipment Spaces for Large Buildings
Fire Pump Room (m2) | 9.25 |  | BASEMENT OR ROOF | From The Architect's Studio Companion, 4, Major Equipment Spaces for Large Buildings
Number of Water Closets (per floor) | 2 |  |  | From The Architect's Studio Companion, 4, Vertical Distribution of Services for Large Buildings
Number of Lavatories (per floor) | 2 |  |  | From The Architect's Studio Companion, 4, Vertical Distribution of Services for Large Buildings
Water Closet and Lavatory Area (m2) | 6
Janitor Closet Area (m2) | 3.4 |  | TYPICAL FLOOR (CORE) | From The Architect's Studio Companion, 4, Vertical Distribution of Services for Large Buildings
VERTICAL TRANSPORTATION
Number of Elevator Shafts | 1 |  |  | From The Architect's Studio Companion, 4, Major Equipment Spaces for Large Buildings
Individual Shaft Area (m2) | 5.75 |  | TYPICAL FLOOR (CORE) | From The Architect's Studio Companion, 4, Major Equipment Spaces for Large Buildings
Elevator Machine Room Area (m2) | 25 |  | ROOF | From The Architect's Studio Companion, 4, Major Equipment Spaces for Large Buildings
EGRESS STAIRS
Width Per Occupant (mm) | 8 |  |  | From The Architect's Studio Companion, 5.2, Sizing the Egress System
Occupant Load | 134.4086 |  |  | From The Architect's Studio Companion, 5.2, Sizing the Egress System
Number of Egress Stairs | 1 |  |  | From The Architect's Studio Companion, 5.2, Sizing the Egress System
Clear Width of Corridor and Stair (m) | 0.9 |  |  | From The Architect's Studio Companion, 5.2, Sizing the Egress System
Length of Egress Stair Enclosure (m) | 3.76 |  | TYPICAL FLOOR (CORE) | From The Architect's Studio Companion, 5.2, Sizing the Egress System
Width of Egress Stair Enclosure (m) | 1.8 |  | TYPICAL FLOOR (CORE)