## CALCULATION
DEDICATED OUTDOOR AIR SYSTEM (DOAS)
|  | Formula | Dimensional Analysis
OCCUPANCY
Program Area (m2) | 5000
Program | Retail - General
Occupant Density Method | ASHRAE 62.1-2022 Occupant Density
User-Defined Density (person/m2)
Code/Standard Density (person/m2) | 0.15
Total People Count | 750
FLOW RATE CALCULATION
Flow Rate Method | ASHRAE 62.1-2022 Flow Rates
Flow Rate per Area (l/s/m2) | 0.6
Flow Rate per Person (l/s/person) | 3.8
User-Defined Flow Rate per Area (l/s/m2)
User-Defined Flow Rate per Person (l/s/person)
Total Flow Rate (l/s) | 5850
Total Flow Rate (m3/s) | 5.85
Air Velocity (m/s) | 8
Safety Factor (%) | 15%
Shaft Area Required (m2) | 1.6819
ALL-AIR SYSTEM (VARIABLE AIR VOLUME OR SIMILAR)
|  | Formula | Dimensional Analysis
Peak Heating Load (kW) | 100
Peak Cooling Load (kW) | 150
Thermostat Cooling Setpoint (°C) | 24
Thermostat Heating Setpoint (°C) | 18
Supply Air Temperature (°C) | 12.8
Specific Heat Capacity of Air (kJ/kg °C) | 1.006
Density of Air (kg/m3) | 1.202
Total Flow Rate in Heating (m3/s) | 15.9036
Total Flow Rate in Cooling (m3/s) | 11.0757
Air Velocity (m/s) | 8
Safety Factor (%) | 15%
Shaft Area Required (m2) | 4.5723
𝑇𝑜𝑡𝑎𝑙 𝑂𝑐𝑐𝑢𝑝𝑎𝑛𝑡𝑠=𝑂𝑐𝑐𝑢𝑝𝑎𝑛𝑡 𝐷𝑒𝑛𝑠𝑖𝑡𝑦 ∗ 𝐴𝑟𝑒𝑎
𝑡𝑜𝑡𝑎𝑙 𝑝𝑒𝑜𝑝𝑙𝑒=𝑝𝑒𝑟𝑠𝑜𝑛/𝑚^2 ∗ 𝑚^2
)
𝑄_𝑡𝑜𝑡𝑎𝑙= 〖(𝑄〗_(𝑎𝑟𝑒𝑎 )∗ 𝐴𝑟𝑒𝑎)+ 〖(𝑄〗_(𝑝𝑒𝑜𝑝𝑙𝑒 )∗ 𝑃𝑒𝑜𝑝𝑙𝑒)
+
𝑙/𝑠=(𝑙/(𝑠 ∙𝑚^2 ) ∗ 𝑚^2 ) + (𝑙/(𝑠 ∙𝑝𝑒𝑟𝑠𝑜𝑛) ∗ 𝑝𝑒𝑜𝑝𝑙𝑒)= 𝑙/(𝑠 ∙1000)= 𝑚^3/𝑠
𝑄_𝑡𝑜𝑡𝑎𝑙=𝑣 ∗ 𝐴 ∗(1+𝑆𝐹)
𝑚^3/𝑠= 𝑚/𝑠∗ 𝑚^2 ∗(1+𝑆𝐹)
𝑄_𝑡𝑜𝑡𝑎𝑙=𝑣 ∗ 𝐴 ∗(1+𝑆𝐹)
𝑚^3/𝑠= 𝑚/𝑠∗ 𝑚^2 ∗(1+𝑆𝐹)
ℎ_𝑠=𝑐_𝑝∗𝜌∗𝑄_𝑡𝑜𝑡𝑎𝑙∗∆𝑇
ℎ_𝑠 (Heating Load)
ℎ_𝑠 (Cooling Load)
𝜌
𝑐_𝑝
𝑘𝑊=𝑘𝐽/𝑠=𝑘𝐽/(𝑘𝑔∙℃) ∗𝑘𝑔/𝑚^3 ∗𝑚^3/𝑠 ∗℃
∆𝑇=Setpoint −Supply Air Temperature

## Lists
| person/m2 | l/s/per | l/s/m2
Commercial - Office Buliding - Lobbies and Corridors | 0.1 | 2.5 | 0.3
Commercial - Office Buliding - Office Space | 0.05 | 2.5 | 0.3
Education - Assembly | 1 | 3.8 | 0.3
Education - Classrooms (5-8) | 0.25 | 5 | 0.6
Education - Classrooms (9+) | 0.35 | 5 | 0.6
Education - Lecture Classroom | 0.65 | 3.8 | 0.3
Education - Lecture Hall | 1.5 | 3.8 | 0.3
Education - Libraries | 0.1 | 2.5 | 0.6
Education - University Laboratory | 0.25 | 5 | 0.9
Public Assembly - Auditorium Seating | 1.5 | 2.5 | 0.3
Public Assembly - Libraries | 0.1 | 2.5 | 0.6
Public Assembly - Museums | 0.4 | 3.8 | 0.3
Retail - General | 0.15 | 3.8 | 0.6
Retail - Mall Common Areas | 0.4 | 3.8 | 0.3
Retail - Supermarket | 0.08 | 3.8 | 0.3
Residential - Common Corridors | 0 | 0 | 0.3
Residential - Living Area | 0.1 | 2.5 | 0.3
ASHRAE 62.1-2022 Occupant Density
User-Defined Occupant Density
ASHRAE 62.1-2022 Flow Rates
User-Defined Flow Rates